## Assessment
Utility | Order | Area | Status | Key Indicators | Key Findings | Key Message
Tagbilaran City Waterworks System | 1 | Strategy & Planning | Moderate | Revised vision, mission and values (Nov 2025); 5 strategic objectives; CAPEX PhP 255.4 M in the plan vs PhP 579.2 M in the financial model (2026–2029) | • New vision: world-class, sustainable waterworks with 24/7 potable supply by 2035. • Five objectives defined: billed volume, NRW, collection, cost recovery, after-sales service. • Three priority projects: pipe replacement (PhP 113.1 M), coverage expansion (PhP 22.9 M), new main lines for bulk water (PhP 119.4 M). • Plan is preliminary; objectives lack owners, annual targets and timelines. • The plan and the financial model are not aligned (CAPEX, OPEX scenario, volume base of the tariff). | Clear direction is in place; objectives now need owners, annual targets and deadlines to become an executable plan.
Tagbilaran City Waterworks System | 2 | Commercial Management | Critical | Tariff unchanged since Sept 2016; PhP 12.5 collected per m3 vs PhP 17.68/m3 cost-recovery tariff (2024); collection efficiency not measured | • Connections grew from 5,612 (2020) to 6,461 (2024) but fell to 6,314 (2025); 99% residential; average consumption 23.6 m3/connection/month. • Billed volume flat at 1.7–1.9 M m3/yr since 2020. • Block tariff unchanged since Sept 2016 (PhP 62 minimum for 10 m3; PhP 7–23/m3; commercial PhP 23/m3; 15% late penalty). • Collections rose from PhP 18.7 M (2020) to PhP 23.1 M (2023) and PhP 22.9 M (2024); billings are not recorded, so collection efficiency cannot be measured. • Collections per m3 (PhP 12.5) look high for the 2016 tariff and need to be reconciled. • Meters are purchased by customers and are not always replaced when required. | A 2016 tariff, flat volumes and no billing records make the revenue base the critical constraint.
Tagbilaran City Waterworks System | 3 | Technical Operations | Moderate | NRW 39.9% (Level 1); NRW 21.6 l/conn/h (Level 3); continuity 23.9 h/day, 93% of customers 24/7 (Level 4); availability 168 l/cap/day (Level 4) | • NRW 46% (2023) and 40% (2024); 31% in H1 2025 is provisional because several production readings are repeated month to month. • Production is declining: 9.7 MLD (2023), 8.4 MLD (2024), 7.7 MLD (H1 2025). • 26 pumping units (160.5 HP) on deep wells, all with production meters and chlorinators. • Old galvanized iron pipes in Tiptip, Manga and Ubujan; no DMAs yet; no preventive maintenance. • Supply gap of 11.7 MLD against projected city demand. | Continuity is good, but about 40% of produced water is lost while production declines; cutting NRW is the cheapest source of new supply.
Tagbilaran City Waterworks System | 4 | Financial Management | Critical | EBITDA margin -12.8% (Level 1); operating cost coverage 88.7% (Level 3); operating ratio 1.13 (2023) | • Revenue PhP 23.1 M vs OPEX PhP 26.1 M (2023): operating loss of about PhP 3.0 M. • Negative bottom line acknowledged by the utility. • Operates as a Local Economic Enterprise (LEE), not funded by the general fund; accounts not yet ring-fenced. • Proposed tariff (PhP 214.03 for the first 10 m3) is based on a volume that includes private providers' water; on TCWS bulk volume alone the required average tariff would be about PhP 50/m3. | Revenues do not cover operating costs; tariff reform and ring-fenced LEE accounts are required for cost recovery.
Tagbilaran City Waterworks System | 5 | Human Resources | Moderate | 9 regular staff + 15 job-order (24 total, 6 female); 1.39 regular staff per 1,000 connections (Level 5); 3.7 including job-order | • Lean staffing ratio, well below the 1:250 industry average. • Heavy reliance on job-order staff (63% of workforce). • Multi-tasking of personnel and unclear organizational structure. • Training needs in technical, finance, billing and collection, management and water safety planning. • No data on turnover or HR costs. | The team is lean and committed but stretched; formalize the structure and invest in technical, finance and billing skills.
Tagbilaran City Waterworks System | 6 | Water Quality & Safety | Moderate | Drinking water quality 90% (Level 3) | • 10% of samples fail national drinking water standards (PNSDW). • Chlorinators installed in all pump stations. • Water quality monitoring and compliance identified as a weakness. | Disinfection is in place, but a 10% sample failure rate requires a water safety plan and stronger monitoring.
Tagbilaran City Waterworks System | 7 | Coverage & Inclusion | Weak | Water coverage 27% of city population (Level 1); approx. 33% of households in the 10 served barangays | • Serves 10 of 15 barangays; other providers (BWUI, Richli) supply most of the city. • Expansion to Cabawan, Booy, Cogon, Dampas and Bool planned; 11,908 households to benefit by 2039. • TCWS does not provide sanitation services. | Coverage is low even inside its own service area; expansion depends on new supply and investment.
Tagbilaran City Waterworks System | 8 | Data & Performance Management | Weak | 10 of 22 performance indicators can be calculated; 19 data inconsistencies found across sources | • No data on billings, metering, customer satisfaction, complaints, turnover or HR costs; no 2024 OPEX. • Connection breakdown by barangay is repeated unchanged across 2022–2025 records. • Production readings repeated month to month in 2025; some units at zero in late 2024. • Business plan, financial model and utility records report different connections, NRW, CAPEX and revenue labels. | Data quality is a binding constraint; reconcile one set of baseline figures before setting targets.

## Key_Messages
Utility | Order | Type | Message
Tagbilaran City Waterworks System | 1 | Overall | TCWS provides reliable water to its customers but is not financially sustainable: the tariff has not changed since 2016, about 40% of produced water is lost, and revenues fall short of operating costs.
Tagbilaran City Waterworks System | 2 | Overall | Average performance level across the 10 measurable indicators: 2.9 of 5 (between Basic and Good).
Tagbilaran City Waterworks System | 3 | Priority 1 | Raise revenue: adjust the tariff toward cost recovery, linked to visible service improvements.
Tagbilaran City Waterworks System | 4 | Priority 2 | Reduce NRW from 40% to 20% through DMAs, pipe replacement and control of illegal connections.
Tagbilaran City Waterworks System | 5 | Priority 3 | Fix the data: record billings, verify production meters, and align the plan with the financial model.
Tagbilaran City Waterworks System | 6 | Priority 4 | Ring-fence the waterworks account and assign owners and deadlines to each objective.
Tagbilaran City Waterworks System | 7 | Priority 5 | Build staff capacity in technical operations, finance, billing and water safety.

## SWOT
Utility | Category | Order | Item | Source
Tagbilaran City Waterworks System | Strength | 1 | Committed and customer-friendly staff | Utility SWOT
Tagbilaran City Waterworks System | Strength | 2 | Staff can work under pressure | Utility SWOT
Tagbilaran City Waterworks System | Strength | 3 | Already a Local Economic Enterprise (LEE), not funded by the general fund | Utility SWOT
Tagbilaran City Waterworks System | Strength | 4 | Chlorinators installed in all pumping stations | Utility SWOT
Tagbilaran City Waterworks System | Strength | 5 | Responsive team, especially in emergency services | Utility SWOT
Tagbilaran City Waterworks System | Strength | 6 | Customer expectations are effectively managed | Utility SWOT
Tagbilaran City Waterworks System | Strength | 7 | Strong management support | Utility SWOT
Tagbilaran City Waterworks System | Strength | 8 | Online payment partners | Utility SWOT
Tagbilaran City Waterworks System | Strength | 9 | Reliable supply of 22–24 hours per day | Derived from document
Tagbilaran City Waterworks System | Strength | 10 | Lean staffing ratio (1.4 regular staff per 1,000 connections) | Derived from document
Tagbilaran City Waterworks System | Weakness | 1 | Multi-tasking of personnel (organizational structure) | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 2 | Old galvanized iron pipes (parts of Tiptip, Manga, Ubujan) | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 3 | Need for training of technical and finance personnel | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 4 | Low tariff | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 5 | Lack of training for billing and collection, management and water safety plans | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 6 | Lack of water supply | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 7 | Lack of preventive maintenance | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 8 | Negative bottom line | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 9 | Handling negative criticism | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 10 | Lack of decision-making | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 11 | Water quality monitoring and compliance (10% failure in sampling) | Utility SWOT
Tagbilaran City Waterworks System | Weakness | 12 | High NRW (40% in 2024) and no district metered areas | Derived from document
Tagbilaran City Waterworks System | Weakness | 13 | Billings not recorded, so collection efficiency cannot be measured | Derived from document
Tagbilaran City Waterworks System | Weakness | 14 | Low coverage (about 27% of city population) | Derived from document
Tagbilaran City Waterworks System | Weakness | 15 | Tariff unchanged since September 2016 | Derived from document
Tagbilaran City Waterworks System | Weakness | 16 | Declining production (9.7 MLD in 2023 to 7.7 MLD in H1 2025) | Derived from document
Tagbilaran City Waterworks System | Weakness | 17 | Inconsistent data across records, plan and financial model | Derived from document
Tagbilaran City Waterworks System | Opportunity | 1 | Availability of bulk water supply in a few years | Utility SWOT
Tagbilaran City Waterworks System | Opportunity | 2 | Large growth potential; many investors | Utility SWOT
Tagbilaran City Waterworks System | Opportunity | 3 | NGOs and private organizations that help improve water services (e.g., USAID, Maynilad) | Utility SWOT
Tagbilaran City Waterworks System | Opportunity | 4 | Support from other local water utilities (collaboration with BWUI) | Utility SWOT
Tagbilaran City Waterworks System | Opportunity | 5 | Proposed tariff is financially viable and affordable (2% of low-income household income) | Derived from document
Tagbilaran City Waterworks System | Opportunity | 6 | Expansion to 5 unserved barangays; 11,908 households to benefit by 2039 | Derived from document
Tagbilaran City Waterworks System | Opportunity | 7 | City commitment to digitalize billing and keep TCWS public | Derived from document
Tagbilaran City Waterworks System | Threat | 1 | Climate change | Utility SWOT
Tagbilaran City Waterworks System | Threat | 2 | Natural hazards such as typhoons and earthquakes (standby gensets in selected pump stations) | Utility SWOT
Tagbilaran City Waterworks System | Threat | 3 | Saltwater intrusion in water sources | Utility SWOT
Tagbilaran City Waterworks System | Threat | 4 | Deep well sources of private institutions, establishments and businesses | Utility SWOT
Tagbilaran City Waterworks System | Threat | 5 | Competition from other water providers in the city (BWUI, Richli) | Derived from document
Tagbilaran City Waterworks System | Threat | 6 | Rising electricity costs (power is the largest projected OPEX item) | Derived from document
Tagbilaran City Waterworks System | Threat | 7 | Customer resistance to tariff increases without visible service improvement | Derived from document